## hydraulic data sheet
Hydraulic data sheet & simulation control page
site parameters |  |  | hydraulic data points |  |  |  | system output table
static head (m) | 7 | entry | flow rate | intake loss | pipe loss | net head | turbine speed | delivered power | arrival volts | current
max flow available (l/sec) | 56 | no. | (l/sec) | (mbar) | (mbar) | (m) | (RPM) | (W) | (V) | (A)
pipe diameter (mm) | 134 | 1 | 8 | 0 | 23 | 6.7652 | 8.2986 | -0.1336 | 5.6833 | -0.024486
|  | 2 | 9 | 0 | 29 | 6.7039 | 35.522 | 1.0155 | 23.5975 | 0.044828
speed as %age of abs. freewheel speed |  | 3 | 10 | 1 | 35 | 6.6324 | 89.5629 | 16.3893 | 58.6282 | 0.29119
minimum speed | 26% | 4 | 11 | 1 | 41 | 6.5712 | 143.1281 | 41.9188 | 93.6886 | 0.46607
maximum speed | 55% | 5 | 12 | 1 | 48 | 6.4997 | 169.1903 | 74.4962 | 109.9946 | 0.70549
|  | 6 | 13 | 1 | 56 | 6.418 | 194.7973 | 110.1014 | 126.1706 | 0.909
|  | 7 | 14 | 1 | 64 | 6.3363 | 208.8132 | 147.4066 | 134.4303 | 1.1422
hydraulic data point |  | 8 | 15 | 1 | 73 | 6.2445 | 226.827 | 185.0168 | 145.624 | 1.3234
entry no. | 23 | 9 | 16 | 1 | 82 | 6.1526 | 239.397 | 222.2721 | 153.1322 | 1.512
|  | 10 | 17 | 2 | 91 | 6.0505 | 251.1363 | 258.4663 | 160.1794 | 1.6808
|  | 11 | 18 | 2 | 102 | 5.9382 | 258.1244 | 293.051 | 163.9834 | 1.8615
values at current MPP estimate |  | 12 | 19 | 2 | 112 | 5.8361 | 265.1449 | 326.2354 | 167.8979 | 2.024
calc sheet entry no | 12 | 13 | 20 | 2 | 123 | 5.7237 | 274.7944 | 357.2056 | 173.7973 | 2.1409
speed (as % of freewheel) | 41.95% | 14 | 21 | 2 | 135 | 5.6012 | 275.2354 | 385.6999 | 173.2227 | 2.3194
maximum power (W) | 510.5074 | 15 | 22 | 3 | 147 | 5.4685 | 278.6697 | 411.3094 | 174.8891 | 2.4498
turbine speed (RPM) | 276.701 | 16 | 23 | 3 | 160 | 5.3358 | 281.9 | 434.4496 | 176.4977 | 2.5641
arrival volts (V) | 170.2868 | 17 | 24 | 3 | 173 | 5.203 | 284.9216 | 455.0747 | 178.0437 | 2.6625
current (A) | 3.1228 | 18 | 25 | 3 | 187 | 5.0601 | 285.6457 | 472.3505 | 178.0356 | 2.7637
|  | 19 | 26 | 4 | 201 | 4.907 | 285.5303 | 486.0425 | 177.5279 | 2.8519
|  | 20 | 27 | 4 | 215 | 4.764 | 285.5191 | 497.9093 | 177.1504 | 2.9278
|  | 21 | 28 | 4 | 230 | 4.6109 | 285.0029 | 506.0692 | 176.5184 | 2.9864
|  | 22 | 29 | 4 | 246 | 4.4475 | 279.9087 | 510.3328 | 172.6512 | 3.079
|  | 23 | 30 | 5 | 262 | 4.2739 | 276.701 | 510.5074 | 170.2868 | 3.1228
|  | 24 | 31 | 5 | 279 | 4.1004 | 276.5157 | 507.7658 | 170.2403 | 3.1069
|  | 25 | 32 | 5 | 296 | 3.9268 | 270.5999 | 502.0915 | 166.0667 | 3.1494
Note on K5: includes allowance for DC converter losses

## generator datasheet
Baldor DC generator datasheet
model | voltage | power | RPM | max current | max torque | resistance | bEMF const | torque const | visc. friction
| Vnom | (kW) | RPM | Im | Tm | R | Ke | Kt | Dv
VP/CDP3320 | 90 | 0.25 | 1750 | 3.2 | 1.36 | 3.51 | 0.42982 | 0.42982 | 0.00073295
VP/CDP3330 | 90 | 0.37 | 1750 | 4.8 | 2.04 | 2.326 | 0.43018 | 0.43018 | 0.0011242
VP/CDP3335 | 90 | 0.37 | 1750 | 5 | 1.43 | 0.821 | 0.46871 | 0.46871 | 0.0011242
VP/CDP3440 | 90 | 0.56 | 1750 | 7 | 3.06 | 1.077 | 0.44997 | 0.44997 | 0.0017437
VP/CDP3445 | 90 | 0.75 | 1750 | 10 | 4.08 | 0.96 | 0.43872 | 0.43872 | 0.0023633
VP/CDP3316 | 180 | 0.25 | 1750 | 1.6 | 1.36 | 5.178 | 0.93701 | 0.93701 | 0.00073295
VP3416 | 180 | 0.25 | 1750 | 1.6 | 1.36 | 9.403 | 0.90012 | 0.90012 | 0.00073295
VP3426 | 180 | 0.37 | 1750 | 2.4 | 2.04 | 6.909 | 0.89173 | 0.89173 | 0.0011242
VP/CDP3326 | 180 | 0.37 | 1750 | 2.5 | 2.04 | 3.454 | 0.93509 | 0.93509 | 0.0011242
VP/CDP3436 | 180 | 0.56 | 1750 | 3.7 | 3.06 | 3.367 | 0.91423 | 0.91423 | 0.0017437
VP/CDP3455 | 180 | 0.75 | 1750 | 5 | 4.08 | 2.477 | 0.91463 | 0.91463 | 0.0023633
VP/CDP3575 | 180 | 1.12 | 1750 | 7.7 | 6.12 | 1.52 | 0.91835 | 0.91835 | 0.0035697
VP/CDP3585 | 180 | 1.51 | 1750 | 9.6 | 8.16 | 1.109 | 0.92412 | 0.92412 | 0.0048413
VP/CDP3603 | 180 | 2.23 | 1750 | 14 | 12.24 | 0.547 | 0.94043 | 0.94043 | 0.0072868
VP/CDP3605 | 180 | 3.73 | 1750 | 24.5 | 20.4 | 0.367 | 0.93315 | 0.93315 | 0.012145
Select generator to be evaluated and paste below. Then go to calculation sheet.
model | voltage | power | RPM | max current | max torque | resistance | bEMF const | torque const | visc. friction
VP/CDP3455 | 180 | 0.75 | 1750 | 5 | 4.08 | 2.477 | 0.91463 | 0.91463 | 0.0023633
^ ^ ^ ^ PASTE selected generator above this line ^ ^ ^ ^

## calculation sheet
turbine parameters
width (mm) | 180 | turbine |  |  |  | generator | [6 empty] | transmission & delivery |  |  | water-to-wire
diameter (mm) | 265 | speed range | speed |  | output power | ω | ω | Tg | Ig | Vg | Wg | efficiency | transmission loss |  | arrival volts | delivered power | efficiency
visc.friction coeff (Nm/(rad/sec) | 0.068 | (%age) | rad/sec | RPM | (W) | rad/sec | RPM | (Nm) | (A) | (V) | (W) | (%) | (V) | (%) | (V) | (W) | (%)
|  | 26% | 17.9589 | 171.4952 | 585.8524 | 125.7126 | 1200.4667 | 4.4272 | 4.5156 | 103.7955 | 468.703 | 84.21% | 10.8375 | 10.44% | 92.9579 | 402.974 | 32.07%
speed as %age of absolute freewheel speed |  | 27.45% | 18.9605 | 181.0594 | 604.6601 | 132.7235 | 1267.4158 | 4.328 | 4.389 | 110.5215 | 485.0812 | 84.45% | 10.5337 | 9.531% | 99.9878 | 421.2948 | 33.53%
minimum speed | 26% | 28.9% | 19.9621 | 190.6236 | 622.0031 | 139.7344 | 1334.3649 | 4.2288 | 4.2624 | 117.2475 | 499.7562 | 84.57% | 10.2298 | 8.725% | 107.0177 | 437.9067 | 34.85%
maximum speed | 55% | 30.35% | 20.9636 | 200.1877 | 637.8814 | 146.7453 | 1401.314 | 4.1295 | 4.1358 | 123.9735 | 512.7279 | 84.61% | 9.9259 | 8.006% | 114.0476 | 452.8095 | 36.04%
|  | 31.8% | 21.9652 | 209.7519 | 652.2948 | 153.7562 | 1468.2631 | 4.0303 | 4.0092 | 130.6995 | 523.9963 | 84.56% | 9.622 | 7.362% | 121.0775 | 466.0033 | 37.09%
hydraulic parameters |  | 33.25% | 22.9667 | 219.316 | 665.2435 | 160.767 | 1535.2122 | 3.931 | 3.8825 | 137.4256 | 533.5614 | 84.43% | 9.3181 | 6.78% | 128.1074 | 477.4881 | 38%
dynamic head (m) | 4.2739 | 34.7% | 23.9683 | 228.8802 | 676.7275 | 167.7779 | 1602.1613 | 3.8318 | 3.7559 | 144.1516 | 541.4233 | 84.22% | 9.0142 | 6.253% | 135.1373 | 487.2638 | 38.78%
flow rate (l/sec) | 30 | 36.15% | 24.9698 | 238.4443 | 686.7466 | 174.7888 | 1669.1104 | 3.7326 | 3.6293 | 150.8776 | 547.5819 | 83.93% | 8.7104 | 5.773% | 142.1672 | 495.3306 | 39.42%
|  | 37.6% | 25.9714 | 248.0085 | 695.301 | 181.7997 | 1736.0595 | 3.6333 | 3.5027 | 157.6036 | 552.0373 | 83.57% | 8.4065 | 5.334% | 149.1971 | 501.6883 | 39.93%
|  | 39.05% | 26.9729 | 257.5727 | 702.3906 | 188.8106 | 1803.0086 | 3.5341 | 3.3761 | 164.3296 | 554.7893 | 83.14% | 8.1026 | 4.931% | 156.227 | 506.337 | 40.3%
generation/transmission parameters |  | 40.5% | 27.9745 | 267.1368 | 708.0155 | 195.8215 | 1869.9577 | 3.4348 | 3.2495 | 171.0556 | 555.8381 | 82.64% | 7.7987 | 4.559% | 163.2569 | 509.2767 | 40.53%
coupling step-up ratio | 7 | 41.95% | 28.9761 | 276.701 | 712.1756 | 202.8324 | 1936.9068 | 3.3356 | 3.1228 | 177.7817 | 555.1836 | 82.06% | 7.4948 | 4.216% | 170.2868 | 510.5074 | 40.63%
coupling efficiency (%age) | 95% | 43.4% | 29.9776 | 286.2651 | 714.8709 | 209.8433 | 2003.8559 | 3.2364 | 2.9962 | 184.5077 | 552.8259 | 81.4% | 7.1909 | 3.897% | 177.3168 | 510.029 | 40.59%
cable resistance (ohm) | 2.4 | 44.85% | 30.9792 | 295.8293 | 716.1015 | 216.8542 | 2070.8051 | 3.1371 | 2.8696 | 191.2337 | 548.7648 | 80.67% | 6.887 | 3.601% | 184.3467 | 507.8417 | 40.42%
DC converter efficiency (%age) | 96% | 46.3% | 31.9807 | 305.3935 | 715.8673 | 223.8651 | 2137.7542 | 3.0379 | 2.743 | 197.9597 | 543.0005 | 79.84% | 6.5832 | 3.326% | 191.3766 | 503.9453 | 40.11%
|  | 47.75% | 32.9823 | 314.9576 | 714.1683 | 230.876 | 2204.7033 | 2.9386 | 2.6164 | 204.6857 | 535.5329 | 78.93% | 6.2793 | 3.068% | 198.4065 | 498.3399 | 39.66%
turbine constants |  | 49.2% | 33.9838 | 324.5218 | 711.0046 | 237.8869 | 2271.6524 | 2.8394 | 2.4897 | 211.4118 | 526.3621 | 77.93% | 5.9754 | 2.826% | 205.4364 | 491.0255 | 39.08%
flow rate const (l/sec/m^0.5) | 18.5717 | 50.65% | 34.9854 | 334.0859 | 706.3761 | 244.8978 | 2338.6015 | 2.7402 | 2.3631 | 218.1378 | 515.488 | 76.82% | 5.6715 | 2.6% | 212.4663 | 482.002 | 38.36%
rotation const (rad/sec/m^0.5) | 33.4113 | 52.1% | 35.987 | 343.6501 | 700.2828 | 251.9087 | 2405.5506 | 2.6409 | 2.2365 | 224.8638 | 502.9106 | 75.6% | 5.3676 | 2.387% | 219.4962 | 471.2696 | 37.51%
|  | 53.55% | 36.9885 | 353.2142 | 692.7248 | 258.9196 | 2472.4997 | 2.5417 | 2.1099 | 231.5898 | 488.6299 | 74.25% | 5.0637 | 2.187% | 226.5261 | 458.8281 | 36.52%
|  | 55% | 37.9901 | 362.7784 | 683.702 | 265.9305 | 2539.4488 | 2.4424 | 1.9833 | 238.3158 | 472.646 | 72.77% | 4.7599 | 1.997% | 233.556 | 444.6776 | 35.39%
system performance variables
hydraulic
full flow rate (l/sec) | 38.3942
part flow fraction (ratio) | 0.78137
max turbine eff. at this flow | 62.85%
hydraulic power (W) | 1256.5354
abs. freewheel speed (rad/sec) | 69.0728
stall torque (Nm) | 45.7338
Note on A24: value is full flow rate/sqrt(head)
Note on A25: value is theoretical frictionless freewheel rotational speed /sqrt(head)
Note on B6: take as 0.068

## turbine efficiency curve
|  |  |  | Coulomb | viscous
model | resistance | bEMF const | torque const | friction | friction
| R | Ke | Kt | Dc | Dv | parameters
| 6 | 0.285 | 0.2 | 0.036 | 0 | shape factor | 20
[6 empty] | min flow fraction as %age of full flow | 18%
[6 empty] | max flow fraction as %age of full flow | 100%
[6 empty] | efficiency constant | 1.52
| flow fraction | efficiency |  |  |  | nozzle size fraction | 0.095
| 18% | 0%
| 22.1% | 18.48%
| 26.2% | 30.76%
| 30.3% | 39.36%
| 34.4% | 45.6%
| 38.5% | 50.24%
| 42.6% | 53.72%
| 46.7% | 56.37%
| 50.8% | 58.38%
| 54.9% | 59.89%
| 59% | 61%
| 63.1% | 61.81%
| 67.2% | 62.35%
| 71.3% | 62.68%
| 75.4% | 62.83%
| 79.5% | 62.84%
| 83.6% | 62.71%
| 87.7% | 62.47%
| 91.8% | 62.14%
| 95.9% | 61.72%
| 100% | 61.23%